Cable ID: 0.56CU CAT6A FTP20180406
Test Summary: PASS
Operator: XU HAO
Model: DTX-1800
Date / Time: 04/07/2018 12:47:16am
Software Version: 2.1200
Main S/N: 9557049
Headroom: 5.9 dB (NEXT 12-45)
Limits Version: 1.2800
Remote S/N: 9557050
Test Limit: TIA Cat 6A Channel
NVP: 74.0%
Main Adapter: DTX-CHA001
Cable Type: Cat 6A FTP
Remote Adapter: DTX-CHA001
Wire Map (T568B)
324 ft
PASS
1
1
2
2
Length (ft), Limit 328
[Pair 78]
324
dB
Insertion Loss
3
3
60
Prop. Delay (ns), Limit 555
476
6
6
Delay Skew (ns), Limit 50
31
48
4
4
Resistance (ohms)
[Pair 36]
13.1
5
5
36
7
7
24
8
8
12
Insertion Loss Margin (dB)
[Pair 36]
9.8
S
S
0
Frequency (MHz)
[Pair 36]
498.0
0
Frequency (MHz)
500
Limit (dB)
[Pair 36]
49.2
Worst Case Margin
Worst Case Value
dB
NEXT
dB
NEXT @ Remote
PASS
MAIN
SR
MAIN
SR
100
100
Worst Pair
12-45
12-45
12-45
12-45
80
80
NEXT (dB)
5.9
6.1
15.7
15.0
60
60
Freq. (MHz)
6.3
6.4
442.0
479.0
Limit (dB)
59.9
59.8
27.6
26.6
40
40
Worst Pair
12
45
12
12
20
20
PS NEXT (dB)
7.6
7.7
16.7
16.7
0
0
Freq. (MHz)
6.3
6.4
441.0
473.0
0
Frequency (MHz)
500
0
Frequency (MHz)
500
Limit (dB)
57.4
57.2
24.7
23.9
dB
ACR-F
dB
ACR-F @ Remote
PASS
MAIN
SR
MAIN
SR
100
100
Worst Pair
12-36
78-12
12-36
78-12
80
80
ACR-F (dB)
5.1
6.3
5.1
6.4
60
60
Freq. (MHz)
497.0
344.0
497.0
497.0
Limit (dB)
9.3
12.5
9.3
9.3
40
40
Worst Pair
36
12
36
12
20
20
PS ACR-F (dB)
6.5
6.3
6.5
6.3
0
0
Freq. (MHz)
497.0
497.0
497.0
497.0
0
Frequency (MHz)
500
0
Frequency (MHz)
500
Limit (dB)
6.3
6.3
6.3
6.3
dB
RL
dB
RL @ Remote
PASS
MAIN
SR
MAIN
SR
60
60
Worst Pair
78
78
78
78
48
48
RL (dB)
6.7
8.0
13.3
11.2
36
36
Freq. (MHz)
38.8
50.0
425.0
186.0
24
24
Limit (dB)
16.1
15.0
6.0
9.3
12
12
Compliant Network Standards:
10BASE-T
100BASE-TX
100BASE-T4
0
0
1000BASE-T
10GBASE-T
ATM-25
0
Frequency (MHz)
500
0
Frequency (MHz)
500
ATM-51
ATM-155
100VG-AnyLan
TR-4
TR-16 Active
TR-16 Passive
LinkWare Version 6.2
Project: DEFAULT
Site: D-LAN
UNTITLED.flw